## calculation- Alburquerque
R134a
Pressure | P | unit(Psi)
Low pressure | P1 (Evaporator Side) | 50
High Pressure | P2 (Condenser Side) | 250
Position | Enthaply | Value (Btu/lbm) | Temperature | Value (F)
Evaporator Outlet/Comperssor inlet | h1 | 108.81 | t1 | 40.23
Compressor outlet/Condenser inlet | h2 | 123.554 | t2 | 153.001
Condenser Outlet/Expansion valve inlet | h3 | 60.616 | t3 | 141.79
Expansion valve outlet/Evaporator Inlet | h4 | 60.616 | t4
Calculation of the mass flow rate of refrigerant
Capacity
Tons | 3
Btu/hr (Q_ref) | 36000
M_ref | 747
Work done (compressor) (Btu/hr) | 11013.768
Calculation of the mass of air (Without evaporative media )
Temperature (F)
Enthalpy of air (Inlet of condenser) (Btu/lbm) | 21.626 | 90
Enthalpy of air (Outlet of condenser) (Btu/lbm) | 25.8999 | 107
Q_cond | 47015
M_air | 11001
cfm | 2446
Calculation (With evaporative media)
Specific humidity of the air at the inlet (lb per lb of da) | 0.0122
Specific humidity of the air at the outlet (lb per lb of da) (Rh=100%) | 0.0168
Specific humidity of the air at the outlet (lb per lb of da) (n=80%) | 0.01588
Faucet Temperature
Alburquerque (F) | 76.2
hfg (76.2F) (Btu/lbm) | 1050.29
Q_cond_new | 42519.6043
M_water | 40.4837
T3' | h3' | M_ref_new | Q_ref | Difference | Check
141.79 | 60.616 | 675.5792 | 32558.8644 | 3441.1356 | FALSE
130 | 56.47 | 633.8263 | 33174.4691 | 2825.5309 | FALSE
120 | 52.941 | 602.1498 | 33641.5075 | 2358.4925 | FALSE
110 | 49.41 | 573.4733 | 34064.3139 | 1935.6861 | FALSE
100 | 47.059 | 555.8482 | 34324.1791 | 1675.8209 | FALSE | Temp | differnce
90 | 44.118 | 535.2687 | 34627.6026 | 1372.3974 | FALSE | 41 | 0
80 | 40 | 508.8877 | 35016.5638 | 983.4362 | FALSE
70 | 36.47 | 488.2597 | 35320.7038 | 679.2962 | FALSE
60 | 34.117 | 475.414 | 35510.0999 | 489.9001 | FALSE
50 | 30.588 | 457.3673 | 35776.1815 | 223.8185 | FALSE
40 | 27.0588 | 440.6396 | 36022.8143 | -22.8143 | TRUE
30 | 24.706 | 430.1514 | 36177.4522 | -177.4522 | TRUE
20 | 21.176 | 415.3197 | 36396.13 | -396.13 | TRUE
10 | 17.647 | 401.4806 | 36600.1745 | -600.1745 | TRUE
0 | 14.118 | 388.534 | 36791.0593 | -791.0593 | TRUE
-10 | 10.58 | 376.3663 | 36970.4598 | -970.4598 | TRUE
-20 | 5.88 | 361.3339 | 37192.0974 | -1192.0974 | TRUE
-30 | 3.529 | 354.2562 | 37296.4504 | -1296.4504 | TRUE
-40 | 1.176 | 347.4448 | 37396.8776 | -1396.8776 | TRUE
-50 | -2.352 | 337.7091 | 37540.421 | -1540.421 | TRUE
-60 | -4.706 | 331.511 | 37631.8057 | -1631.8057 | TRUE
-70 | -7.059 | 325.5388 | 37719.8596 | -1719.8596 | TRUE
-80 | -8.235 | 322.6339 | 37762.6895 | -1762.6895 | TRUE

## calculation- Las Vegas
R134a
Pressure | P | unit(Psi)
Low pressure | P1 (Evaporator Side) | 50
High Pressure | P2 (Condenser Side) | 250
Position | Enthaply | Value (Btu/lbm) | Temperature | Value (F)
Evaporator Outlet/Comperssor inlet | h1 | 108.81 | t1 | 40.23
Compressor outlet/Condenser inlet | h2 | 123.554 | t2 | 153.001
Condenser Outlet/Expansion valve inlet | h3 | 60.616 | t3 | 141.79
Expansion valve outlet/Evaporator Inlet | h4 | 60.616 | t4
Calculation of the mass flow rate of refrigerant
Capacity
Tons | 3
Btu/hr (Q_ref) | 36000
M_ref | 747
Work done (compressor) (Btu/hr) | 11013.768
Calculation of the mass of air (Without evaporative media )
|  | Temperature (F) | wbt
Enthalpy of air (Inlet of condenser) (Btu/lbm) | 26.436 | 109 | 67 |  | 128 | 30.767
Enthalpy of air (Outlet of condenser) (Btu/lbm) | 34.6 | 144 |  |  | 129 | 31.008
[5 empty] | 143.9046 | 34.6
Q_cond | 47015
M_air | 5759
cfm | 1280
Calculation (With evaporative media)
Specific humidity of the air at the inlet (lb per lb of da) | 0.0046
Specific humidity of the air at the outlet (lb per lb of da) (Rh=100%) | 0.014246
Specific humidity of the air at the outlet (lb per lb of da) (n=80%) | 0.012317
Faucet Temperature
Las Vegas(F) | 76
hfg (76.2F) (Btu/lbm) | 1050.29
Q_cond_new | 46675.9917
M_water | 44.4411
T3' | h3' | M_ref_new | Q_ref | Difference | Check
141.79 | 60.616 | 741.6186 | 35741.567 | 258.433 | FALSE
130 | 56.47 | 695.7843 | 36417.3485 | -417.3485 | TRUE
120 | 52.941 | 661.0113 | 36930.0409 | -930.0409 | TRUE
110 | 49.41 | 629.5316 | 37394.1776 | -1394.1776 | TRUE
100 | 47.059 | 610.1836 | 37679.4452 | -1679.4452 | TRUE |  | Temp | differnce
90 | 44.118 | 587.5924 | 38012.529 | -2012.529 | TRUE |  | 137.2813 | 0
80 | 40 | 558.6326 | 38439.512 | -2439.512 | TRUE
70 | 36.47 | 535.9881 | 38773.3824 | -2773.3824 | TRUE
60 | 34.117 | 521.8868 | 38981.2924 | -2981.2924 | TRUE
50 | 30.588 | 502.0759 | 39273.384 | -3273.384 | TRUE
40 | 27.0588 | 483.7131 | 39544.1258 | -3544.1258 | TRUE
30 | 24.706 | 472.1997 | 39713.8799 | -3713.8799 | TRUE
20 | 21.176 | 455.9182 | 39953.934 | -3953.934 | TRUE
10 | 17.647 | 440.7262 | 40177.9243 | -4177.9243 | TRUE
0 | 14.118 | 426.5141 | 40387.4685 | -4387.4685 | TRUE
-10 | 10.58 | 413.1569 | 40584.4058 | -4584.4058 | TRUE
-20 | 5.88 | 396.6551 | 40827.7089 | -4827.7089 | TRUE
-30 | 3.529 | 388.8856 | 40942.2627 | -4942.2627 | TRUE
-40 | 1.176 | 381.4084 | 41052.5069 | -5052.5069 | TRUE
-50 | -2.352 | 370.7209 | 41210.082 | -5210.082 | TRUE
-60 | -4.706 | 363.917 | 41310.3997 | -5310.3997 | TRUE
-70 | -7.059 | 357.361 | 41407.0612 | -5407.0612 | TRUE
-80 | -8.235 | 354.1721 | 41454.0777 | -5454.0777 | TRUE
Faucet Temperature
Las Vegas(F) | 77
hfg (76.2F) (Btu/lbm) | 1049.72
T3' | h3' | M_ref_new | Q_ref | Difference | Check
141.79 | 60.616 | 741.2161 | 35722.1698 | 277.8302 | FALSE
130 | 56.47 | 695.4067 | 36397.5845 | -397.5845 | TRUE
120 | 52.941 | 660.6526 | 36909.9987 | -909.9987 | TRUE
110 | 49.41 | 629.19 | 37373.8835 | -1373.8835 | TRUE
100 | 47.059 | 609.8524 | 37658.9963 | -1658.9963 | TRUE
90 | 44.118 | 587.2735 | 37991.8993 | -1991.8993 | TRUE
80 | 40 | 558.3295 | 38418.6506 | -2418.6506 | TRUE
70 | 36.47 | 535.6973 | 38752.3399 | -2752.3399 | TRUE
60 | 34.117 | 521.6036 | 38960.1369 | -2960.1369 | TRUE
50 | 30.588 | 501.8035 | 39252.0701 | -3252.0701 | TRUE
40 | 27.0588 | 483.4506 | 39522.6649 | -3522.6649 | TRUE
30 | 24.706 | 471.9434 | 39692.3269 | -3692.3269 | TRUE
20 | 21.176 | 455.6708 | 39932.2507 | -3932.2507 | TRUE
10 | 17.647 | 440.487 | 40156.1194 | -4156.1194 | TRUE
0 | 14.118 | 426.2826 | 40365.5499 | -4365.5499 | TRUE
-10 | 10.58 | 412.9327 | 40562.3804 | -4562.3804 | TRUE
-20 | 5.88 | 396.4398 | 40805.5514 | -4805.5514 | TRUE
-30 | 3.529 | 388.6745 | 40920.043 | -4920.043 | TRUE
-40 | 1.176 | 381.2014 | 41030.2274 | -5030.2274 | TRUE
-50 | -2.352 | 370.5198 | 41187.717 | -5187.717 | TRUE
-60 | -4.706 | 363.7195 | 41287.9803 | -5287.9803 | TRUE
-70 | -7.059 | 357.1671 | 41384.5892 | -5384.5892 | TRUE
-80 | -8.235 | 353.9799 | 41431.5803 | -5431.5803 | TRUE
Faucet Temperature
Las Vegas(F) | 78
hfg (76.2F) (Btu/lbm) | 1049.16
T3' | h3' | M_ref_new | Q_ref | Difference | Check
141.79 | 60.616 | 740.8207 | 35703.1129 | 296.8871 | FALSE
130 | 56.47 | 695.0357 | 36378.1673 | -378.1673 | TRUE
120 | 52.941 | 660.3001 | 36890.3081 | -890.3081 | TRUE
110 | 49.41 | 628.8543 | 37353.9455 | -1353.9455 | TRUE
100 | 47.059 | 609.5271 | 37638.9061 | -1638.9061 | TRUE
90 | 44.118 | 586.9602 | 37971.6316 | -1971.6316 | TRUE
80 | 40 | 558.0316 | 38398.1552 | -2398.1552 | TRUE
70 | 36.47 | 535.4115 | 38731.6664 | -2731.6664 | TRUE
60 | 34.117 | 521.3253 | 38939.3527 | -2939.3527 | TRUE
50 | 30.588 | 501.5358 | 39231.1301 | -3231.1301 | TRUE
40 | 27.0588 | 483.1927 | 39501.5806 | -3501.5806 | TRUE
30 | 24.706 | 471.6916 | 39671.152 | -3671.152 | TRUE
20 | 21.176 | 455.4277 | 39910.9478 | -3910.9478 | TRUE
10 | 17.647 | 440.252 | 40134.6971 | -4134.6971 | TRUE
0 | 14.118 | 426.0552 | 40344.0159 | -4344.0159 | TRUE
-10 | 10.58 | 412.7124 | 40540.7413 | -4540.7413 | TRUE
-20 | 5.88 | 396.2283 | 40783.7827 | -4783.7827 | TRUE
-30 | 3.529 | 388.4672 | 40898.2132 | -4898.2132 | TRUE
-40 | 1.176 | 380.998 | 41008.3388 | -5008.3388 | TRUE
-50 | -2.352 | 370.3221 | 41165.7444 | -5165.7444 | TRUE
-60 | -4.706 | 363.5254 | 41265.9542 | -5265.9542 | TRUE
-70 | -7.059 | 356.9765 | 41362.5116 | -5362.5116 | TRUE
-80 | -8.235 | 353.7911 | 41409.4775 | -5409.4775 | TRUE

## Energy saving
|  | Temperature (F) |  | C02 (lbs/MWh) | 846.6
Enthalpy of air (Inlet of condenser) (Btu/lbm) | 21.626 | 90 |  | So2 | 0.155
Enthalpy of air (Outlet of condenser) (Btu/lbm) | 25.955 | 120 |  | Nix | 0.481
M_air
cfm
Position | Enthaply | Value (Btu/lbm) | Temperature | Value (F)
Evaporator Outlet/Comperssor inlet | h1 | 108.81 | t1 | 40.23
Compressor outlet/Condenser inlet | h2 | 123.554 | t2 | 153.001
Condenser Outlet/Expansion valve inlet | h3 | 60.616 | t3 | 141.79 |  | Work done (compressor) (Btu/hr) |  | 11014
Expansion valve outlet/Evaporator Inlet | h4 | 60.616 | t4
S.n | Location | Temperature of water | hfg | Temperature (t3') | h3' | M_ref_new | W_comp_new | W_saving (Btu/hr) | W_saving (KW) | No. of hrs in a day | No of hrs in a year | W_saving (KWh) | % saved | Average % saved
1 | Alburquerque | 76 | 1050.29 | 40 | 27.0588 | 441 | 6503 | 4511 | 1.322 | 14 | 5110 | 6755.6421 | 0.61337 | 0.36
2 | Las Vegas | 76 | 1050.29 | 130 | 56.47 | 696 | 10262 | 752 | 0.22039 | 14 | 5110 | 1126.1899 | 0.10225
|  | unit | Remarks
Total Power consumption | 21.9 | Billion KWh
Total Power consumption | 0.0219 | Billion MWh
CO2 emitted | 18.5405 | Billion lbs | Without media
Saving | 5.256 | Billion KWh
Saving | 0.005256 | Billion Mwh
CO2 reduced | 4.4497 | Billion lbs | With media
Validate | 0.24
S.n | Location | Temperature (t3') (F) | h3' (Btu/lb) | M_ref_new | W_comp_new | W_saving (Btu/hr) | % saving | Average saving
1 | Alburquerque | 40 | 27.0588 | 441 | 6503 | 4511 | 0.40957 | 0.24
2 | Las Vegas | 130 | 56.47 | 696 | 10262 | 752 | 0.068277
Without evaporative media
| Amount | Unit
Total Power consumption | 21.9 | Billion KWh
CO2 emitted | 18.54 | Billion lbs | 4.4496
SO2 | 0.003 | Billion lbs | 0.00072
Nox | 0.011 | Billion lbs | 0.00264
With evaporative media
Total Power consumption | 5.256 | Billion KWh
CO2 emitted | 4.45 | Billion lbs
SO2 | 0.00082 | Billion lbs | 0.27333
Nox | 0.00253 | Billion lbs | 0.23

## Economic Analysis
|  | unit | Remarks
Total Power consumption | 21.9 | Billion KWh
Total Power consumption | 0.0219 | Billion MWh
CO2 emitted | 18.5405 | Billion lbs | Without media
Saving | 5.256 | Billion KWh
Saving | 0.005256 | Billion Mwh
CO2 reduced | 4.4497 | Billion lbs | With media
Co2 reduced per home | 440.5673
Savings in dollars | Rate per KWh | Remarks
Energy price | 0.15
Total energy saving per yr | 0.7884 | in billions
Total households | 10.1 | Million
Saving per home per year | 78.0594
Service life (in years) | 15
Discount rate | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
Present Value (In billions) | 931.8681 | 867.8947 | 810.2299 | 758.1324 | 710.9584 | 668.1478 | 629.2126 | 593.726 | 746.2712

## Sheet1
|  | unit | Remarks
Total Power consumption | 21.9 | Billion KWh
Total Power consumption | 0.0219 | Billion MWh
CO2 emitted | 18.5405 | Billion lbs | Without media
Saving | 5.256 | Billion KWh
Saving | 0.005256 | Billion Mwh
CO2 reduced | 4.4497 | Billion lbs | With media
Savings in dollars | Rate per KWh | Remarks
Energy price | 0.15
Total energy saving | 0.7884 | in billions
No of homes
Service life (in years) | 15
Discount rate | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10%
Present Value (In billions) | 9.4119 | 8.7657 | 8.1833 | 7.6571 | 7.1807 | 6.7483 | 6.355 | 5.9966